## Sheet1
Model |  | GP
Input Voltage Waveform |  | Pure sine wave/ same as input (bypass mode)
Nominal Input Voltage |  | 230Vac
Input voltage range |  | 184~272Vac(UPS): 154~272Vac(APL)
Low Loss Voltage |  | 184Vac±7V(UPS), 154Vac±7V(APL)
Low Loss Return Voltage |  | 194Vac±7V(UPS); 164Vac±7V(APL)
High Loss Voltage |  | >272Vac±7V
High Loss Return Voltage |  | <262Vac±7V
Nominal Input Frequency |  | 50Hz / 60Hz (Auto detection)
Input Frequency range |  | 45-65Hz
Low Loss Frequency |  | 45±1Hz
Low Loss Return Frequency |  | 47±1Hz
High Loss Frequency |  | 65±1Hz
High Loss Return Frequency |  | 63±1Hz
Efficiency (Line Mode) |  | >95% ( Rated R load, battery full charged )
Input Current |  | Max 50A
Transfer Time |  | Typical 10ms
Low DC Cut-off Voltage (Lead-Acid Mode) |  | 42.0Vdc(Based on Program 21, 40Vdc~48Vdc settable)
Low DC Warning SOC (Li Mode) |  | Low DC Cut-off SOC +5%
Low DC Warning Return SOC (Li Mode) |  | Low DC Cut-off SOC +15%
Low DC Cut-off SOC (Li Mode) |  | Default 20%, 5%~49% settable
High DC Recovery Voltage |  | 58Vdc
High DC Cut-off Voltage |  | AGM:60V, FLD:62V, USE or Li Mode: C.V. Voltage + 4.0V
No Load Power Consumption |  | <20W
INVERTER MODEL |  | 6KW
Rated Output Power |  | 6KVA / 6KW
Output Voltage Waveform |  | Pure Sine Wave
Output Voltage Regulation |  | 230Vac±5%
Output Frequency |  | 50Hz
Peak Efficiency |  | 0.94
Overload Protection |  | 10s@110%~150% load; 5s@≥150% load
Surge Capacity |  | 18KVA / 18KW
Nominal DC Input Voltage |  | 48Vdc
Cold Start Voltage (Lead-Acid Mode) |  | Low DC Cut-Off Voltage +2Vdc
Cold Start SOC(Li Mode) |  | >Low DC Cut-off SOC +10%
Low DC Warning Voltage (Lead-Acid Mode) |  | 44.0Vdc @ load < 20% 42.8Vdc @ 20% ≤ load < 50% 40.4Vdc @ load ≥ 50%
Low DC Warning Return Voltage (Lead-Acid Mode) |  | 46.0Vdc @ load < 20% 44.8Vdc @ 20% ≤ load < 50% 42.4Vdc @ load ≥ 50%
Low DC Cut-off Voltage (Lead-Acid Mode) |  | 42.0Vdc @ load < 20% 40.8Vdc @ 20% ≤ load < 50% 38.4Vdc @ load ≥ 50%
INVERTER MODEL |  | 6KW
Operating Temperature Range |  | -20℃ to 50℃ (fan assisted cooling)
Storage temperature |  | -40℃~60℃
Humidity |  | 5% to 95% Relative Humidity (Non-condensing)
Altitude |  | <2000m
Product size(D*W*H) |  | 600x310x155mm
Packing size(D*W*H) |  | 675x385x230mm
N.W.(KG) |  | 29Kg
G.W.(KG) |  | 32Kg
INVERTER MODEL |  | 6KW
Charging Algorithm |  | 3-Step
Max. AC Charging Current |  | 80Amp(@Vip=230Vac)
Bulk Charging Voltage | Flooded Battery | 58.4Vdc
| AGM / Gel Battery | 56.4Vdc
Floating Charging Voltage |  | 54Vdc